Copyright September 2012, Division of Facilities Management, Design and Construction (FMDC)

SECTION 015000 – CONSTRUCTION FACILITIES AND TEMPORARY CONTROLS

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract including General and Supplementary Conditions, Bid Form, and other Division 1 Specification Sections apply to this Section.

SUMMARY

This Section includes requirements for construction facilities and temporary controls including temporary utilities, support facilities, security, and protection.

Temporary utilities include, but are not limited to, the following:

Modify list below to suit Project.

Water service and distribution

Temporary electric power and light

Temporary heat

Ventilation

Telephone service

Sanitary facilities, including drinking water

Storm and sanitary sewer

Support facilities include, but are not limited to, the following:

Modify list below to suit Project.

Field offices and storage sheds

Temporary roads and paving

Dewatering facilities and drains

Temporary enclosures

Hoists and temporary elevator use

Temporary project identification signs and bulletin boards

Waste disposal services

Rodent and pest control

Construction aids and miscellaneous services and facilities

Security and protection facilities include, but are not limited to, to following:

Modify list below to suit Project.

Temporary fire protection

Barricades, warning signs, and lights

Sidewalk bridge or enclosure fence for the site

Environmental protection

SUBMITTALS

Include requirements for submittal of installation drawings of critical temporary utilities, if required.

Temporary Utilities:  Submit reports of tests, inspections, meter readings, and similar procedures performed on temporary utilities.

Delete the requirement below on projects of short duration and on small projects with few temporary utility requirements.

Implementation and Termination Schedule:  Within (15) days of the date established for commencement of the Work, submit a schedule indicating implementation and termination of each temporary utility.

QUALITY ASSURANCE

Regulations:  Comply with industry standards and applicable laws and regulations including, but not limited to, the following:

Modify list below to comply or coordinate with applicable regulations.  Include requirements governing storm drainage.  Disposal of excess excavation and waste material and similar regulations.

Building code requirements

Health and safety regulations

Utility company regulations

Police, fire department, and rescue squad rules

Environmental protection regulations

Standards:  Comply with NFPA 241 “Standard for Safeguarding Construction, Alterations, and Demolition Operations”.  ANSI A10 Series standards for “Safety Requirements for Construction and Demolition”, and NECA Electrical Design Library “Temporary Electrical Facilities”.

Electrical Service:  Comply with NEMA, NECA, and UL standards and regulations for temporary electric service.  Install service in compliance with NFPA 70 “National Electric Code”.

Inspections:  Arrange for authorities having jurisdiction to inspect and test each temporary utility before use.  Obtain required certifications and permits.

PROJECT CONDITIONS

Revise below to minimize temporary use of permanent utilities, or Insert exceptions to provisions.  Discourage attempts to delay activation of standpipes and sprinklers.

Temporary Utilities:  Prepare a schedule indicating dates for implementation and termination of each temporary utility.  At the earliest feasible time, when acceptable to the Owner, change over from use of temporary service to use of permanent service.

Conditions of Use:  Keep temporary services and facilities clean and neat in appearance.  Operate in a safe and efficient manner.  Relocate temporary services and facilities as the Work progresses.  Do not overload facilities or permit them to interfere with progress.  Take necessary fire-prevention measures.  Do not allow hazardous, dangerous, or unsanitary conditions, or public nuisances to develop or persist onsite.

PRODUCTS

MATERIALS

General:  Provide new materials.  If acceptable to the Designer, the Contractor may use undamaged, previously used materials in serviceable condition.  Provide materials suitable for use intended.

Delete materials that are not required.  Add materials as necessary to suit Project.

Lumber and Plywood:  Comply with requirements in Division 6 Section “Rough Carpentry”.

Review subparagraph below with Owner’s insurance carrier.  Modify as necessary to suit Project.

For job-built temporary office, shops, and sheds within the construction area, provide UL-labeled, fire-treated lumber and plywood for framing, sheathing, and siding.

For signs and directory boards, provide exterior-type, Grade B-B high-density concrete form overlay plywood of sized and thicknesses indicated.

For fences and vision barriers, provide minimum 3/9” (9.5mm) thick exterior plywood.

For safety barriers, sidewalk bridges, and similar uses, provide minimum 5/8” (16mm) thick exterior plywood.

Delete two paragraphs below if mobile or prefabricated office units are specified.

Gypsum Wallboard:  Provide gypsum wallboard on interior walls of temporary offices.

Roofing Materials:  Provide UL Class A standard-weight asphalt shingles or UL Class C mineral-surfaced roll roofing on roofs of job-built temporary office, shops, and shed.

Paint:  Comply with requirements of Division 9 Section “Painting”.

For job-built temporary offices, shops, sheds, fences, and other exposed lumber and plywood, provide exterior-grade acrylic-latex emulsion over exterior primer.

For sign panels and applying graphics, provide exterior-grade alkyd gloss enamel over exterior primer.

For interior walls of temporary offices, provide two (2) quarts interior latex-flat wall paint.

Tarpaulins:  Provide waterproof, fire-resistant, UL-labeled tarpaulins with flame-spread rating of (15) or less.  For temporary enclosures, provide translucent, nylon-reinforced laminated polyethylene or polyvinyl chloride, fire-retardant tarpaulins.

Water:  Provide potable water approved by local health authorities.

Delete paragraph below if wood fence or covered walkway is used.  For more security, increase fence height to 8’ (2.5m) or more.

Open-Mesh Fencing:  Provide 0.120” (3mm) thick, galvanized 2” (50mm) chainlink fabric fencing 6’ (2m) high with galvanized steel pipe posts, 1½” (38mm) ID for line posts and 2½” (64mm) ID for corner posts.

EQUIPMENT

General:  Provide new equipment.  If acceptable to the Designer, the Contractor may use undamaged, previously used equipment in serviceable condition.  Provide equipment suitable for use intended.

Delete equipment that is not required.  Add equipment as necessary to suit Project.

Water Hoses:  Provide ¾” (19mm), heavy-duty, abrasion-resistant, flexible rubber hoses 100’ (30m) long, with pressure rating greater than the maximum pressure of the water distribution system.  Provide adjustable shutoff nozzles at hose discharge.

Electrical Outlets:  Provide properly configured, NEMA-polarized outlets to prevent insertion of 110 to 120V plugs into higher voltage outlets.  Provide receptacle outlets equipped with ground-fault circuit interrupters, reset button, and pilot light for connection of power tools and equipment.

Electrical Power Cords:  Provide grounded extension cords.  Use hard-service cords where exposed to abrasion and traffic.  Provide waterproof connectors to connect separate lengths of electric cords if single lengths will not reach areas where construction activities are in progress.  Do not exceed safe length-voltage rating.

Modify paragraph below to suit Project.

Lamps and Light Fixtures:  Provide general service incandescent lamps of wattage required for adequate illumination.  Provide guard cages or tempered-glass enclosures where exposed to breakage.  Provide exterior fixture where exposed to moisture.

Heating Units:  Provide temporary heating units that have been tested and labeled by UL, FM, or another recognized trade association related to the type of fuel being consumed.

Modify paragraph below to add stricter requirements when conditions warrant.

Temporary Offices:  Provide prefabricated or mobile units or similar job-built construction with lockable entrances, operable windows, and serviceable finishes.  Provide heated and air-conditioned units on foundations adequate for normal loading.

Delete paragraph below when fixtures connected to previously installed water and sewer service must be used.

Temporary Toilet Units:  Provide self-contained, single-occupant toilet units of the chemical, aerated re-circulation, or combustion type.  Provide units properly vented and fully enclosed with a glass-fiber-reinforced polyester shell or similar nonabsorbent material.

Fire Extinguishers:  Provide hand-carried, portable, UL-rated, Class A fire extinguishers for temporary offices and similar spaces.  In other locations, provide hand-carried, portable, UL-rated, Class ABC, dry-chemical extinguishers, or a combination of extinguishers of NFPA-recommended classes for the exposures.

Comply with NFPA 10 and NFPA 241 for classification, extinguishing agent, and size required by location and class of fire exposure.

EXECUTION

INSTALLATION

Use qualified personnel for installation of temporary facilities.  Locate facilities where they will serve the Project adequately and result in minimum interference with performance of the Work.  Relocate and modify facilities as required.

Provide each Facility ready for use when needed to avoid delay.  Maintain and modify as required.  Do not remove until facilities are no longer needed or are replaced by authorized use of completed permanent facilities.

TEMPORARY UTILITY INSTALLATION

General:  Engage the appropriate local utility company to install temporary service or connect to existing service.  Where company provides only part of the service, provide the remainder with matching, compatible materials and equipment.  Comply with company recommendations.

Arrange with company and existing users for a time when service can be interrupted, if necessary, to make connections for temporary services.

Provide adequate capacity at each stage of construction.  Prior to temporary utility availability, provide trucked-in services.

Obtain easements to bring temporary utilities to the site where the Owner’s easements cannot be used for that purpose.

Retain subparagraph below to prevent extra cost to Owner

Use Charges:  Cost or use charges for temporary facilities are not chargeable to the Owner or Designer.  Neither the Owner nor Designer will accept cost or use charges as a basis of claims for Change Order.

Add provisions for work not in Contract but served by temporary facilities, if required.

Select from paragraphs below for applicable temporary water service requirements.

Temporary Water Service:  Install water service and distribution piping of sizes and pressures adequate for construction until permanent water service is in use.

Sterilization:  Sterilize temporary water piping prior to use.

Or

Temporary Water Service:  The Owner will provide water for construction purposes from the existing building system.  All required temporary extensions shall be provided and removed by the Contractor.  Connection points and methods of connection shall be designated and approved by the Construction Representative.

Select from paragraphs below for applicable temporary electric power service requirements.

Modify paragraph and subparagraphs below to include special power loads, such as continued operation of the existing facility, while power changeover is being made.

Temporary Electric Power Service:  Provide weatherproof, grounded electric power service and distribution system of sufficient size, capacity, and power characteristics during construction period.  Include meters, transformers, overload-protected disconnects, automatic ground-fault interrupters, and main distribution switch gear.

Modify subparagraph below to suit project if underground service must be provided.

Install electric power service underground, except where overhead service must be used.

Power Distribution System:  Install wiring overhead and rise vertically where least exposed to damage.  Where permitted, wiring circuits not exceeding 125V, AC 20ampere rating, and lighting circuits may be nonmetallic sheathed cable where overhead and exposed for surveillance.

Or

Temporary Electric Power Service:  The Owner will provide electric power for construction lighting and power tools.  Contractors using such services shall pay all costs of temporary services, circuits, outlet, extensions, etc.

Insert additional provisions for power distribution to suit project.

Temporary Lighting:  When overhead floor or roof deck has been installed, provide temporary lighting with local switching.

Insert additional lighting provisions to suit Project.

Install and operate temporary lighting that will fulfill security and protection requirements without operating the entire system.  Provide temporary lighting that will provide adequate illumination for construction operations and traffic conditions.

Select from paragraphs below for applicable temporary heating requirements.

Temporary Heating:  Provide temporary heat required by construction activities for curing or drying of completed installations or for protection of installed construction from adverse effects of low temperatures or high humidity.  Select safe equipment that will not have a harmful effect on completed installations or elements being installed.  Coordinate ventilation requirements to produce the ambient condition required and minimize consumption of energy.

Modify paragraph below as necessary.  LP gas or fuel-oil heaters are commonly used.  Steam or hot water heaters, gas-fired space heaters, or electric unit heaters are also often used.

Heating Facilities:  Except where the Owner authorizes use of the permanent system, provide vented, self-contained, LP gas or fuel-oil heaters with individual space thermostatic control.

Usually retain subparagraph below.  Gasoline-burning and salamander heating units are usually prohibited.

Use of gasoline-burning space heaters, open flame, or salamander heating units is prohibited.

Or

Temporary Heating and Cooling:  The normal heating and/or cooling system of the building shall be maintained in operation during the construction.  Should the Contractor find it necessary to interrupt the normal HVAC service to spaces, which have not been vacated for construction, such interruptions shall be pre-scheduled with the Construction Representative.

Select from paragraphs below for applicable temporary telephone requirements.

Temporary Telephones:  Provide temporary telephone service throughout the construction period for all personnel engaged in construction activities.

Telephone Lines:  Provide telephone lines for the following:

Modify list below to suit Project.

Where an office has more than two (2) occupants, install a telephone for each additional occupant or pair of occupants.

Provide a dedicated telephone for a fax machine in the field office.

Provide a separate line for the Owner’s use.

At each telephone, post a list of important telephone numbers.

Or

Temporary Telephones:  The Owner will provide telephones within the facility.  All construction personnel will be allowed access only to those specific telephones designated by the Construction Representative.

Select from paragraphs below for applicable temporary toilet facility requirements.

Temporary Toilets:  Install self-contained toilet units.  Use of pit-type privies will not be permitted.  Comply with regulations and health codes for the type, number, location, operation, and maintenance of fixtures and facilities.  Install where facilities will best serve the Project’s needs.

Retain subparagraph below with either of the (2) paragraphs above on all but the smallest projects.

Shield toilets to ensure privacy.

Provide separate facilities for male and female personnel.

Provide toilet tissue materials for each facility.

Or

Temporary Toilets:  Use of the Owner’s existing toilet facilities will be permitted, so long as facilities are cleaned and maintained in a condition acceptable to the Owner.  All construction personnel will be allowed access only to those specific facilities designed by the Construction Representative.  At substantial completion, restore these facilities to the condition prevalent at the time of initial use.

Or

Temporary Toilets:  The Owner will provide toilets and associated facilities within the building.  All construction personnel will be allowed access only to those specific facilities designated by the Construction Representative.

Select from paragraphs below for applicable temporary wash facility requirements.  Paragraph below may be excessive for small and medium-sized projects.

Wash Facilities:  Install wash facilities supplied with potable water at convenient locations for personnel involved in handling materials that require wash-up for a health and sanitary condition.  Dispose of drainage properly.  Supply cleaning compounds appropriate for each condition.

Provide paper towels or similar disposable materials for each facility.

Provide covered waste containers for used material.

Retain subparagraph below where required by authorities or recommended for health and safety reason.

Provide safety showers, eyewash fountains, and similar facilities for convenience, safety, and sanitation of personnel.

Or

Wash Facilities:  The Owner will provide wash facilities within the building.  All construction personnel will be allowed access only to those specific facilities designated by the Construction Representative.

Select from paragraphs below for applicable temporary drinking water facilities requirements.

Drinking-Water Facilities:  Provide drinking-water fountains where indicated, including paper cup supply.

Or

Drinking-Water Facilities:  Provide containerized, tap-dispenser, bottled-water drinking-water units, including paper supply.

Where power is accessible, provide electric water coolers to maintain dispensed water temperature at 45°F to 55°F (7°C to 13°C).

Or

Drinking-Water Facilities:  The Owner will provide drinking water facilities within the building.  All construction personnel will be allowed access only to those specific facilities designated by the Construction Representative.

Add any other temporary facilities as required.  Add janitorial services if required.  Add gas or other utility services as required.  Add ventilation or humidity control as required.

Provide earthen embankments and similar barriers in and around excavations and subgrade construction, sufficient to prevent flooding by runoff of storm water from heavy rains.

SUPPORT FACILITIES INSTALLATION

General:  Locate field offices, storage sheds, and other temporary construction and support facilities for easy access.

Maintain support facilities until near Substantial Completion.  Remove prior to Substantial Completion.  Personnel remaining after Substantial Completion will be permitted to use permanent facilities, under conditions acceptable to the Owner.

Modify paragraph below as necessary to suit Project.

Field Offices:  Provide insulated, weathertight temporary offices of sufficient size to accommodate required office personnel at the Project site.  Keep the office clean and orderly for use for small progress meetings.  Furnish and equip office as follows:

Furnish with a desk and chairs, a 4-drawer file cabinet, plan table, plan rack, and a 6-shelf bookcase.

Equip with a water cooler and private toilet complete with water closet, lavatory, and medicine cabinet unit with a mirror.

Insert additional subparagraphs to include other equipment, such as fax machines, copying machines, computers, and additional items of furniture as needed.

Select from paragraphs below for applicable temporary storage facility requirements.  Modify or expand paragraphs as required to suit Project.

Storage facilities:  Install storage sheds sized, furnished, and equipped to accommodate materials and equipment involved, including temporary utility service.  Sheds may be open shelters or fully enclosed spaces within the building or elsewhere onsite.

Or

Storage Facilities:  Limited areas for storage of building materials are available onsite.  Available storage areas are shown on the drawings.  The Contractor shall provide his own security.  Specific locations for storage and craning operations will be discussed at the Pre-Bid Meeting and the Pre-Construction Meeting.

Or

Storage Facilities:  The Owner will provide storage onsite as designated by the Facility Representative or the Construction Representative.  Areas for use by the Contractor for storage will be identified at the Pre-Bid Meeting.

Or

Storage Facilities:  No areas for storage of building materials can be made available onsite except for on the roof.  Loads shall not exceed the loading limits as stated on the drawings.  Roofing materials must be craned onto the roof from dedicated parking spaces as arranged by the Contractor with the City; costs of all such arrangements shall be paid by the Contractor.  The Contractor shall provide his own security as he finds necessary.  Specific locations for storage and craning operations will be discussed at the Pre-Bid Meeting and the Pre-Construction Meeting.

Or

Storage Facilities:  No areas for storage of building materials can be made available onsite.  The Contractor shall provide for all storage offsite.  All off-site storage locations shall be approved by the Construction Representative.  The Contractor shall provide his own security as he finds necessary.  The Construction Representative shall have access to the off-site storage at all times.

Retain paragraph below if temporary paving is required.  Modify as required to suit Project.  Temporary paving is assumed to be asphalt.  Revise if temporary paving is to be another material.

Temporary Paving:  Construct and maintain temporary roads and paving to support the indicated loading adequately and to withstand exposure to traffic during the construction period.  Locate temporary paving for roads, storage areas, and parking where the same permanent facilities will be located.  Review proposed modifications to permanent paving with the Designer.

Paving:  Comply with Division 2 Section “Hot-Mixed Asphalt Paving” for construction and maintenance of temporary paving.

Coordinate temporary paving development with subgrade grading, compaction, installation and stabilization of subbase, and installation of base and finish courses of permanent paving.

Install temporary paving to minimize the need to rework the installations and to result in permanent roads and paved areas without damage or deterioration when occupied by the Owner.

Delay installation of the final course of permanent asphalt concrete paving until immediately before Substantial Completion.  Coordinate with weather conditions to avoid unsatisfactory results.

Extend temporary paving in and around the construction area as necessary to accommodate delivery and storage of materials, equipment usage, administration, and supervision.

Insert provisions to indicate depth of pavement and temporary traffic controls, if required.

Select from paragraphs below for applicable temporary toilet facility requirements.  Revise as required to suit Project.

Construction Parking:  Parking at the site will be provided in the areas designated at the Pre-Construction Meeting.

Or

Construction Parking:  Contractors must be prepared to discuss their storage and parking needs at the Pre-Bid Meeting.  Parking for construction personnel cannot be provided onsite.  All parking will be offsite.  The Contractor will have to park on the street, in city-owned lots, or in commercial lots.  Under no circumstances will any vehicle be parked in a fire lane.  Parking on lawns shall be prohibited.

Paragraph below contains only basic requirements.  Modify as required to suit Project.

Dewatering Facilities and Drains:  For temporary drainage and dewatering facilities and operations not directly associated with construction activities included under individual Sections, comply with dewatering requirements of applicable Division 2 Sections.  Where feasible, utilize the same facilities.  Maintain the site, excavations, and construction free of water.

Temporary enclosures are required on most Projects at some time during construction.  Modify as necessary to suit Project.

Temporary Enclosures:  Provide temporary enclosures for protection of construction, in progress and completed, from exposure, foul weather, other construction operations, and similar activities.

Where heat is needed and the permanent building enclosure is not complete, provide temporary enclosures where there is no other provision for containment of heat.  Coordinate enclosure with ventilating and materials drying or curing requirements to avoid dangerous conditions and effects.

Install tarpaulins securely with incombustible wood framing and other materials.  Close openings of 25SqFt (2.3SqM) or less with plywood or similar materials.

Close openings through floor or roof decks and horizontal surfaces with load-bearing, wood-framed construction.

Retain subparagraph below for large and high-rise projects.  Provisions may be too expensive for small projects.

Where temporary wood or plywood enclosure exceeds 100SqFt (9.2SqM) in area, use UL-labeled, fire-retardant-treated material for framing and main sheathing.

Delete paragraph below for low-rise construction of less than (3) stories.

Temporary Lifts and Hoists:  Provide facilities for hoisting materials and employees.  Truck cranes and similar devices used for hoisting materials are considered “tools and equipment” and not temporary facilities.

Select from paragraphs below for applicable temporary elevator usage.  Modify as required to suit Project.

Temporary Elevator Use:  Refer to Division 14 for Elevators.

Or

Temporary Elevator Use:  The Owner will allow use of elevators within the building.  All construction personnel will be allowed access only to those specific elevators designated by the Construction Representative.

Delete paragraph below unless signs are specificly approved by the Project Manager.  Revise as required to suit Project.

Project Identification and Temporary Signs:  Prepare project identification and other signs of size indicated.  Install signs where indicated to inform the public and persons seeking entrance to the Project.  Support on posts or framing of preservative-treated wood or steel.  Do not permit installation of unauthorized signs.

Project Identification Signs:  Engage an experienced sign painter to apply graphics.  Comply with details indicated.

Temporary Signs:  Prepare signs to provide directional information to construction personnel and visitors.

Revise paragraph below as desired.  Insert specific requirements, such as parking lot lighting and illumination of project identification sign.

Temporary Exterior Lighting:  Install exterior yard and sign lights so signs are visible when Work is being performed.

Collection and Disposal of Waste:  Collect waste from construction areas and elsewhere daily.  Comply with requirements of NFPA 241 for removal of combustible waste material and debris.  Enforce requirements strictly.  Do not hold materials more than seven (7) days during normal weather or three (3) days when the temperature is expected to rise above 80°F (27°C).  Handle hazardous, dangerous, or unsanitary waste materials separately from other waste by containerizing properly.  Dispose of material lawfully.

Add references to approved disposal methods.  Cross-reference sections that specify handling of special waste material.  See evaluations for for further discusin and sample text.

Delete paragraph eblow only when cost considerations are paramount.  Expand if specific pests such as termites or pigeons are known to be a problem.

Rodent Pest Control:  Before deep foundation work has been completed, retain a local exterminator or pest control company to recommend practices to minimize attraction and harboring of rodents, roaches, and other pests.  Employ this service to perform extermination and control procedures are regular intervals so the Project will be free of pests and their residues at Substantial Completion.  Perform control operations lawfully, using environmentally safe materials.

Stairs:  Until permanent stairs are available, provide temporary stairs where ladders are not adequate.  Cover finished, permanent stairs with a protective covering of plywood or similar material so finishes will be undamaged at the time of acceptance.

Individual Project circumstances may require use of other construction aids and miscellaneous facilities such as walkways, scaffoldings, platforms, swing stages, ramps and bridges, incidental sheeting and shoring, demolition waste chutes, and similar construction aids.  Add requirements as necessary to suit Project.

SECURITY AND PROTECTION FACILITIES INSTALLATION

Modify paragraph below if it does not represent desired arrangement.

Except for use of permanent fire protection as soon as available, do not change over from use of temporary security and protection facilities to permanent facilities until Substantial Completion, or longer, as requested by the Designer.

Paragraph below specifies currently accepted requirements.  Modify to suit local conditions.

Temporary Fire Protection:  Until fire-protection needs are supplied by permanent facilities, install and maintain temporary fire-protection facilities of the types needed to protect against reasonable predictable and controllable fire losses.  Comply with NFPA 10 “Standard for Portable Fire Extinguishers” and NFPA 241 “Standard for Safeguarding Construction, Alterations, and Demolition Operations”.

Locate fire extinguishers where convenient and effective for their intended purpose, but not less than one (1) extinguisher on each floor at or near each usable stairwell.

Store combustible materials in containers in fire-safe locations.

Maintain unobstructed access to fire extinguishers, fire hydrants, temporary fire-protection facilities, stairways, and other access routes for fighting fires.  Prohibit smoking in hazardous fire-exposure areas.

Provide supervision of welding operations, combustion-type temporary heating units, and similar sources of fire ignition.

Permanent Fire Protection:  At the earliest feasible date in each area of the Project complete installation of the permanent fire-protection facility including connected services and place into operation and use.  Instruct key personnel on use of facilities.

When sprinkler systems or other permanent fire-protection systems are used, add specific requirements.

Barricades, Warning Signs, and Lights:  Comply with standards and code requirements for erection of structurally adequate barricades.  Paint with appropriate colors, graphics, and warning signs to inform personnel and the public of the hazard being protected against.  Where appropriate and needed, provide lighting including flashing red or amber lights.

Delete paragraph below for restricted city and urban sites where a combination fence and covered walkway or sidewalk bridge will be used.

Enclosure Fence:  Before excavation begins, install an enclosure fence with lockable entrance gates.  Locate where indicated, or enclose the entire site or the portion determined sufficient to accommodate construction operations.  Install in a manner that will prevent people, dogs, and other animals from easily entering the site, except by the entrance gates.

Provide open-mesh, chainlink fencing with posts set in a compacted mixture of gravel and earth.

Retain subparagraph above when chainlink fencing is acceptable.  Retain subparagraph below when a solid, framed wood fence is required.

Provide plywood fence, 8’ (2.5m) high, framed with (4) 2”x4” (50mm x 100mm) rails, and preservative-treated wood posts spaced not more than 8’ (2.5m) apart.

Delete paragraph below where covered walkways are not required and there is sufficient area to conduct operations including delivery, include installation details on drawings.

Covered Walkway:  Erect a structurally adequate, protective covered walkway for passage of persons along the adjacent public street.  Coordinate with entrance gates, other facilities, and obstructions.  Comply with regulations of authorities having jurisdiction.

Construct covered walkways using scaffold or shoring framing.  Provide wood plank overhead decking, protective plywood enclosure walls, handrails, barricades, warning signs, lights, safe and well-drained walkways, and similar provisions for protection and safe passage.  Extend the back wall beyond the structure to complete the enclosure fence.  Paint and maintain in a manner acceptable to the Owner and the Designer.

Retain paragraph below because the enclosure fence does not always provide adequate security against theft and vandalism.

Security Enclosure and Lockup:  Install substantial temporary enclosure of partially completed areas of construction.  Provide locking entrances to prevent unauthorized entrance, vandalism, theft, and similar violations of security.

Storage:  Where materials and equipment must be stored and are of value or attractive for theft, provide a secure lockup.  Enforce discipline in connection with the installation and release of material to minimize the opportunity for theft and vandalism.

Environmental Protection:  Provide protection, operate temporary facilities, and conduct construction in ways and by methods that comply with environmental regulations and minimize the possibility that air, waterways, and subsoil might be contaminated or polluted or that other undesirable effects might result.  Avoid use of tools and equipment that produce harmful noise.  Restrict use of noisemaking tools and equipment to hours that will minimize complaints from persons or firms near the site.

OPERATION, TERMINATION AND REMOVAL

Paragraph below is important where allowances for metered use of temporary facilities have been established.

Supervision:  Enforce strict discipline in use of temporary facilities.  Limit availability of temporary facilities to essential and intended uses to minimize waste and abuse.

Maintenance:  Maintain facilities in good operating condition until removal.  Protect from damage by freezing temperatures and similar elements.

Maintain operation of temporary enclosures, heating, cooling, humidity control, ventilation, and similar facilities on a 24-hour basis where required to achieve indicated results and to avoid possibility of damage.

Protection:  Prevent water-filled piping from freezing.  Maintain markers for underground lines.  Protect from damage during excavation operations.

Termination and Removal:  Unless the Designer requests that it be maintained longer, remove each temporary facility when the need has ended, when replaced by authorized use of a permanent facility, or no later than Substantial Completion.  Complete or, if necessary, restore permanent construction that may have been delayed because of interference with the temporary facility.  Repair damaged Work, clean exposed surfaces, and replace construction that cannot be satisfactorily repaired.

Materials and facilities that constitute temporary facilities are the Contractor’s property.  The Owner reserves the right to take possession of project identification signs.

Consider inserting specific removal requirements as illustrated below.

Remove temporary paving not intended for or acceptable for integration into permanent paving.  Where the area is intended for landscape development, remove soil and aggregate fill that do not comply with requirements for fill or subsoil in the area.  Remove materials contaminated with road oil, asphalt and other petrochemical compounds, and other substances that might impair growth of plant materials or lawns.  Repair or replace street paving, curbs, and sidewalks at the temporary entrances as required by the governing authority.

At Substantial Completion, clean and renovate permanent facilities used during the construction period including, but not limited to, the following:

Check subparagraphs below for conflict or duplication with provisions in other Sections, particularly Divisions 15 and 16.

Replace air filters and clean inside of ductwork and housing.

Replace significantly worn parts and parts subject to unusual operating conditions.

Replace lamps burned out or noticeably dimmed by hours of use.

END OF SECTION  015000